## Slide 1: An introduction to openstudio and energyplus
Edward Vuong

## Slide 2: Who am I?
What I do
  Road cycling
  Whole building optimization
    Codes development (Retrofit & carbon code)
    Gas Heat pump
    Modelling tool development
What NRC’s Construction Research Centre does
  Building envelope material development/testing
  Building acoustics (transmission prediction, signal processing, perception assessment)
  Indoor air quality (airborne transmission, arctic HRV/ERV application)
  Climate resiliency adaptation (overheating, resiliency, future looking climate data)

## Slide 3: The Goal of this Workshop
By the end, participants should be able to:
Model using OpenStudio
Ask questions
Figure 1. Energy transfers in a building (Payette, 2018)

## Slide 4: Overview
What is BEM?
SketchUp our building (exercise)
OpenStudio – Envelope (exercise)
OpenStudio – Internal loads (exercise)
HVAC Overview
OpenStudio – HVAC (exercise)
Energy Conservation Measures
OpenStudio Parametric Analysis Tool (exercise)

## Slide 5: Building energy modelling (BEM)
Characterize energy and moisture
  Between the building and the external environment
  Within the building
For example…
  Power generation
  Battery charging
  People
  “everything”
Figure 1. Energy transfers in a building (Payette, 2018)

## Slide 6: When to….
Skip BEM
Measurement and verification
Alterations/Retrofit
  Heuristics
  Utility bills
Garbage input (garbage output)
  Uncertain input
Simpler alternative
USE BEM
Code compliance
Explain or justify
  Physical phenomenon (academic)
  What happens to X when Y occurs? (professional)
  Forecast/predict hypotheticals (academic + professional)
Exploratory
Calibration

## Slide 7: BEM Tools: EnergyPlus & OpenStudio
E+ is a building energy simulation program
Detail physics
Funded by the US DOE: 1997- present
Open-source
“No user interface”  intended as an engine
  DesignBuilder, Autodesk Revit, Trace3D Plus
OpenStudio Project
US DOE: 2008 – present; open-source
Several pieces of software and tools
  OpenStudio Application – “OpenStudio”
  OpenStudio SketchUp plug-in
  Parametric Analysis Tool
  OpenStudio SDK, OpenStudio-Standards, OpenStudio Server
The rest of “car”

## Slide 8: BEM Tools: EnergyPlus & OpenStudio
OpenStudio Project (cont.)
  Contributions from
    US Labs (ORNL, LBNL, NREL, PNNL, ANL)
    Private organizations (OpenStudio-Coalition)
    Industry & academia (Autodesk, Carrier, Trane, individual firms, professionals/academics)
    “Canadian content” (NRCan, NRC)
  Continuous development, reliable, free, community
  Limited tech support
    IES, Trace3D, DesignBuilder
SketchUp
  3D CAD
  Architectural/interior design
  Plug-ins

## Slide 9: General procedures for modelling buildings
Building information need:
Geometry
Construction details
  Air leakage
Internal loads
Schedule and setpoints
HVAC
  Components, HVAC drawings (zoning)
Domestic hot water

## Slide 10: Zoning (thermal zones)
Volume of air with a single average temperature
The building we’re in right now
Approximate as a box with air
  Avoid temperature variations
  Entire building – too coarse
Rule of thumbs
  Similar activity/occupancy, HVAC, orientation/location (windows)
No single right answer
Figure 2. Ft. Monmouth floor plan (GARD Analytics and University of Illinois, 2003)

## Slide 11: Zoning (thermal zones)
Figure 3. Ft. Monmouth floor plan zoned (GARD Analytics and University of Illinois, 2003)

## Slide 12: Zoning (thermal zones)
Differences: Cooling load < 10%, Heating load < 1%
Is this acceptable?
Figure 4a. Ft. Monmouth zone cooling load and Figure 4b Ft. Monmouth 1 & 6 zone cooling load (GARD Analytics and University of Illinois, 2003)

## Slide 13: Simulation Parameters
Timestep
  Discrete time intervals
  “Usually” 10 - 15 min
Shadow calculation
  Shadows cast by building, shading devices
  OS default: 20 day average (daylighting modelling – more frequent)
Ground temperature
  Gradual change
  Can be significant for residential; less for commercial
Autosizing
  Eqp capacity, flowrate, load, fan power
  Sizing factor
  Sequential & uniform loading
  Design day
    ASHRAE design day conditions

## Slide 14: Exercise: Let’s sketchup our building
Create a model
Canadian Centre for Housing Technology research facility
  NZER
  Semi-detached
  150 m2
  Side by side comparison
  CCHT-F is the test facility (left)
  500 sensors (incl. assembly)
  Gas, electricity, water
OS_exercise>sketchup>CCHT_plans “CCHT-F” plans
  3_sketchup_exercise.pdf
  4 zones
Figure 5. CCHT E and F

## Slide 15: building envelope
Envelope – walls, roofs, floor, fenestration (doors, windows, skylights)
Construction – assembly of layers of materials that form the envelope
Thermal bridge (thermal bypass) – areas of an construction that allows heat to easily flow through
  Studs, balconies, window perimeters
  Derates insulation (R-value)
    E.g. 77% insulation & 23% stud vs 100% insulation
  Extensive guide from Morrison Hershfield
Figure 6. Wall cross section (Morrison-Hershfield, 2018)

## Slide 16: Air Leakage
Unintended outdoor air leaking into (infiltration) or out of (exfiltration) the building
Blower door test
  Closed up vs as-operated
Figure 7. Blower door test fan

## Slide 17: Air Leakage
Blower door test cont.
  Guarded vs unguarded
  Negative, positive, single/multi-point (pressure)
  ACH50, Flow coefficient, Effective leakage area (4Pa or 10Pa), flow per exterior area (75Pa)
Figure 8. Unguarded blower door test
Figure 8. Guarded blower door test

## Slide 18: Exercise: Air leakage modelling
Characterizing the air leakage rate
Converting leakage rates from one pressure to another (4._os_envelope_exercise.pdf)

## Slide 19: Openstudio exercise: envelope
Insulated surfaces
  Blu_wall: R-28 (U-value 0.198 W/m2∙K)
  Ground_floor: R-18 (U-value 0.319 W/m2∙K)
  Attic floor/second storey ceiling - R-53 (U-value 0.106 W/m2∙K)
Uninsulated surfaces
  Roof
  Interior surfaces
  doors
Adiabatic partitions
Window
  U-value 0.83 W/m2∙K

## Slide 20: Internal Loads in OpenStudio
Sources of heat that warms up a building
  Light
  Occupants
  Plug (receptacle) and process loads
Different “types of heat” in modelling
Lighting
  Convected, visible (short wave), long wave, return air
  Max power
    entered in internal gains object
Occupants
  Sensible, latent, radiant
  Activity level (W per person)
    Entered as a schedule
Plug or process
  Convected, radiant, loss (e.g. exhausted)
  Don’t use the nameplate value (nominal power)
    Exceptions: electric resistive, constant load

## Slide 21: Sources for internal gain data
Lighting
  ASHRAE Fundamental
  EnergyPlus Input Output Reference document (Table 1.28) (from ASHRAE 1282 RP)
  ASHRAE Fundamental 2021: Chapter 18 – Table 3 for lighting heat gain
Occupancy
  ASHRAE Fundamental 2021: Chapter 18 – Table 1
  https://www.cambeep.eng.cam.ac.uk/system/files/documents/internalheat.pdf
Plug/process loads
  ASHRAE Fundamental 2021 - Chapter 18 - Table 4A to Table 11
  http://hes-documentation.lbl.gov/calculation-methodology/calculation-of-energy-consumption/heating-and-cooling-calculation/internal-gains
NBC 2020 – Table 9.36.5.4 for Residential Buildings
  NBC 2020 and NECB 2020
  Code compliance modelling default

## Slide 22: Schedules in Openstudio
Control equipment and events
Control logic (1 for on, 0 for off)
Temperature setpoints
Number of occupants
Occupant activity level
Temperature, power, fractions, dimensionless

## Slide 23: OpenStudio Exercise: Internal Loads
OS_exercise > openstudio-gains
  5_os_internal_gains_exercise.pdf
  internal_gains_schedule_data.xlsx
    Heat gain fractions
    Occupant activity
    Schedule fractions
  internal_gain_reference_tables.pdf
    Data tables from ASHRAE Fundamentals and EnergyPlus I/O doc

## Slide 24: An Overview of HVAC systems and equipment
Purpose: condition and ventilate a space
Types of HVAC: Centralized and Decentralized
  Centralized
    Boiler + pump + baseboards/radiators
    Chillers + pumps + water coils
  Decentralized
    Window air conditioners
    Electric baseboards
Packaged, Split, Unitary
  Interchangeable?

## Slide 25: An Overview of HVAC systems and equipment
Unitary - An HVAC system comprised of one or more factory built assemblies
Packaged – a single package
Figure 9. Packaged system (Petro Home Services, 2023)

## Slide 26: An Overview of HVAC systems and equipment
Split system
  More than one assembly
  Indoor separated from outdoor
  Multi-split
  Ducted
Figure 10. Split system (Petro Home Services, 2023)

## Slide 27: An Overview of HVAC systems and equipment
Split cont.
  Ductless
Figure 11. Mini-split (Fujitsu General , 2023)

## Slide 28: OpensTudio HVAC
Air and water based
  Conditioning air/water and circulating it
  Sometimes brine instead of water
Fundamental/component level view
Heating
  Electric coil, gas coil, direct expansion coil, water coil
Cooling
  Cooling tower, chiller, direct expansion coil, water coil

## Slide 29: Ventilation: HRV & ERV
Introduce outdoor air
Exhaust stale indoor air
Opportunity to save energy by preheat/cooling
  Heat recovery ventilator (HRV)
  Energy recovery ventilator (ERV)

## Slide 30: Ventilation: HRV
Thermal energy only  heat
Leakage (cross contamination)
Figure 12. ERV schematic (U.S. Department of Energy, 2021)

## Slide 31: Ventilation: ERV
Heat and moisture  energy exchange
ERV core
  Cross flow
  Moisture wicking material
Enthalpy wheel
  Rotating wheel
  Same type of material as a core
  Inside view
Cross contamination
Figure 13. ERV core (Mitsubishi Electric Sales Canada, 2021)

## Slide 32: Examples of HVAC systems
Central air conditioner (AC) and furnace
  Common
  Single package or separate equipment
Cold climate air source heat pump
  No formal definition
  Rated capacity 3.52 kW @ -8.3 oC
  70% of the -8.3 oC rated capacity @ -15 oC
  COP 1.8 @ -15 oC

## Slide 33: Openstudio exercise: HVAC + DHW
Constant volume central AC + NG furnace
  Air conditioner: COP 3
  Condensing furnace: AFUE 96%
  Rotary ERV (~ 50% effectiveness
  Only first and second floor conditioned
  Single thermostat
    Heating: 21 oC; Cooling: 24 oC
Domestic hot water
  Demand
    Peak flow demand: 0.000083 ~ 300 L/hr
    OS_exercises > openstudio-hvac
      dhw_load_profile.osm
  Electric water heater
    UA-factor: 1.3 W/K
    100 % efficiency
    Located in first_storey
    2 hour recovery (for sizing)
  Pump head 300 Pa
Zone | Volume (m3) | ELA (cm2)
Attic | 259.01 | 51
First_storey | 199.14 | 40
Second_storey | 217.92 | 43
Misc.
  Air leakage test results:
    Whole building ELA = 134 cm2
      Assume cracks/gaps uniformly distributed based on volume

## Slide 34: Things to be mindful of
NZER  low EUI
  ERV defrost model limited (no degradation due to ice)
  Ground temperature 18oC
    Difficult to capture
    Kiva model
HVAC control is basic
  EnergyPlus EMS
Rigid loop structure
Limited features in OpenStudio App
Work-a-rounds

## Slide 35: Openstudio (EnergyPlus) Results
EnergyPlus output files
DesignBuilder results viewer (free)
EnergyPlus Reports
  Summary tables
  LEED summary

## Slide 36: BEM and Standards/Guidelines
ASHRAE Standard 140
  “Pseudo-standard” for BEM
ASHARE Guideline 14 (calibration)
  Procedure and standard for estimating energy, water and demand savings
  Normalized mean bias error (NME)– 10%
  Coefficient of variation of the root-mean-square error (CV-RSME)– 30%
Ruleset schema and checker – ASHRAE P229
  Common ruleset model report (RMR) schema
  Ruleset checking tool (RCT)

## Slide 37: OpenStudio references and help
EnergyPlus Documentation
  EnergyPlus web-based documentation
  Official Quickstart
  Lecture ppt
  Kiva ground heat transfer model
OpenStudio Documentation
  OpenStudio App + SketchUp for OS
  YouTube
    OpenStudio + SketchUp
    NREL
  OpenStudio SDK
OpenStudio Support
  Unmet Hours
  Energy Models
EnergyPlus Support
  Official EnergyPlus Support

## Slide 38: Energy Conservation Measures (ECM)
aka Energy efficiency measures (EEM)
Strategies for saving energy
  Upgrade
  New system
  Repair?
Examples
  Windows & insulation
  Better boiler/water heater/fans
  Window-wall ratio
  Leakage control
  Better control/automation

## Slide 39: Applying ECM in Openstudio
Changing insulation
  Increase material thickness
  Swap material
  New construction
Changing the window-wall ratio
  Delete/add new window (redraw)
OpenStudio Measures
  De-risk, synergize, scale
    More data, consistency, productivity, shareable
  Commands delete/add/swap/alter a model  single package
  Go through an example

## Slide 40: OpenStudio measures
Ruby script
  Instructions that control programs
  Interpreted vs compiled (program)
  Ruby is an interpreted language e.g. python, matlab, javascript
Sources for OpenStudio measures
Measure writers are not omnipotent
Example: multiple measures
Example: create prototype
Measure walkthrough & OpenStudio-Standards

## Slide 41: Parametric Study
Multiple ECMs and inputs  combinations
Small scale parametric study
  Improve CCHT F’s envelope
  A few ECMs
    South WWR (0.35, 0.45, 0.55, 0.65)
    Wall R-value (R-20, R-40, R-60)
  OpenStudio App
    12 simulations in series
    12 files in parallel
Parametric Analysis Tool
  1 file
  12 alternatives
  Example
Case # | WWR | Wall R-value
case_1 | 0.35 | R-20
case_2 | 0.35 | R-40
case_3 | 0.35 | R-60
case_4 | 0.45 | R-20
case_5 | 0.45 | R-40
case_6 | 0.45 | R-60
case_7 | 0.55 | R-20
case_8 | 0.55 | R-40
case_9 | 0.55 | R-60
case_10 | 0.65 | R-20
case_11 | 0.65 | R-40
case_12 | 0.65 | R-60

## Slide 42: Parametric Analysis Tool
Large(r) scale analyses
  More than a few ECMs
  Investigating the performance of a system (as a measure)
    Vary building
    Vary location
  Retrofit portfolio of buildings
    Building type, location
  Automated optimization
    Full factorial experiment
    Particle swarm
    Genetic algorithm

## Slide 43: References
Fujitsu General . (2023). What is a Mini-Split? Retrieved from Fujitsu General United States & Canada: https://www.fujitsugeneral.com/us/residenGARD Analytics, & University of Illinois. (n.d.). Lecture 07 Building Modeling Questions.
EnergyPlus University Course Teaching Material. Retrieved from https://energyplus.net/assets/nrel_custom/eplus_files/university_course.zip.
Fujitsu General . (2023). What is a Mini-Split? Retrieved from Fujitsu General United States & Canada: https://www.fujitsugeneral.com/us/residential/what-is-a-mini-split.html
Mitsubishi Electric Sales Canada. (2021). How it works: Energy Recovery Ventilator Cores. Markham: Mitsubishi Electric Sales Canada. Retrieved from https://www.mitsubishitechinfo.ca/sites/default/files/010_HiW%20Energy%20Recovery%20Cores.pdf
Morrison Hershfield. (2018). Morrison-Hershfield. Retrieved from https://www.bchydro.com/content/dam/BCHydro/customer-portal/documents/power-smart/builders-developers/building-envelope-thermal-bridging-guide-v1-6.pdf
Payette. (2018, November 7). Energy modeling and the whole building approach to energy efficiency. Energy Modeling and the Whole Building Approach to Energy Efficiency. Retrieved February 19, 2023, from https://www.payette.com/news/energy-modeling-and-the-whole-building-approach-to-energy-efficiency/
Petro Home Services. (2023). HVAC Packaged Unit vs. Split System: Differences, benefits, and how to choose. Retrieved from Petro Home Services: https://www.petro.com/resource-center/hvac-packaged-unit-vs-split-system
Tec tube. (2017, September 26). Fundamentals of Energy Recovery Ventilators (ERVs) [Video]. US: Youtube. Retrieved from https://www.youtube.com/watch?v=QOSelUK6dpQ&t=100s
U.S. Department of Energy. (2021). EnergyPlus Version 9.6.0 Documentation: Input Output Reference. NREL.